## Carleton
Classroom HVAC Master Sheet - Carleton Campus (updated August 12th)
Building Name | Room Number | Room Type | Pre-COVID Capacity | Area (sq.ft) | Room Height (ft) | Air Flow (CFM) | Air Changes per Hr (ACH) | Ocuppant Density | Original HVAC Assessment | Post Verification Assessment | Source of Air Volume Data
BURBIDGE | 216 | Special Purpose Teaching | 21 | 1823 | 9 | 1707 | 7.3441 | 86.8095 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
BURBIDGE | 318 | Tiered /Fixed Classroom | 95 | 887 | 9 | 917 | 8.1084 | 9.3368 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
BURBIDGE | SEM1 | Classroom | 12 | 260 | 9 | 475 | 14.3288 | 21.6667 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM10 | Classroom | 12 | 191 | 9 | 483 | 19.8337 | 15.9167 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
BURBIDGE | SEM13 | Classroom | 12 | 225 | 9 | 250 | 8.7146 | 18.75 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM14 | Classroom | 12 | 225 | 9 | 250 | 8.7146 | 18.75 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM15 | Classroom | 12 | 210 | 9 | 250 | 9.3371 | 17.5 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM2 | Classroom | 12 | 260 | 9 | 145 | 4.3741 | 21.6667 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM3 | Classroom | 12 | 260 | 9 | 135 | 4.0724 | 21.6667 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM4 | Classroom | 12 | 260 | 9 | 140 | 4.2232 | 21.6667 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM5 | Classroom | 12 | 260 | 9 | 130 | 3.9216 | 21.6667 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM6 | Classroom | 12 | 260 | 9 | 130 | 3.9216 | 21.6667 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM7 | Classroom | 12 | 260 | 9 | 137 | 4.1327 | 21.6667 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM8 | Classroom | 12 | 318 | 9 | 160 | 3.9462 | 26.5 | Measurement & Verification Required | Standard | Verfied - HVAC design drawings (current project)
BURBIDGE | SEM9 | Classroom | 12 | 191 | 9 | 337 | 13.8384 | 15.9167 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CLIN RES CTR | C122 | Classroom | 6 | 270 | 10 | 466 | 12.183 | 45 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CLIN RES CTR | C206 | Classroom | 17 | 516 | 10.5 | 1379 | 17.9663 | 30.3529 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CLIN RES CTR | C216 | Classroom | 6 | 195 | 11 | 448 | 14.7429 | 32.5 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CLIN RES CTR | C-223 | Classroom | 5 | 154 | 10.5 | 471 | 20.561 | 30.8 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
COLLABORATIVE HEALTH EDUC BLDG | C140 | Flat Floor Classroom | 66 | 1572 | 11 | 3375 | 13.7772 | 23.8182 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C150 | Flat Floor Classroom | 66 | 1590 | 11 | 3375 | 13.6212 | 24.0909 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C170 | Flat Floor Classroom | 200 | 5937 | 11 | 11250 | 12.1598 | 29.685 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C220 | Classroom | 15 | 375 | 11 | 650 | 11.123 | 25 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C221 | Classroom | 15 | 375 | 11 | 650 | 11.123 | 25 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C241 | Classroom | 6 | 195 | 11 | 238 | 7.8322 | 32.5 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C251 | Classroom | 6 | 198 | 11 | 238 | 7.7135 | 33 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C261 | Classroom | 8 | 190 | 11 | 363 | 12.2601 | 23.75 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C263 | Classroom | 8 | 188 | 11 | 325 | 11.0934 | 23.5 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C264 | Flat Floor Classroom | 60 | 1317 | 11 | 2925 | 14.2521 | 21.95 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C266 | Flat Floor Classroom | 30 | 773 | 11 | 1938 | 16.0884 | 25.7667 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C268 | Flat Floor Classroom | 30 | 804 | 11 | 2175 | 17.3597 | 26.8 | Standard | Standard | Verified - HVAC design drawings
COLLABORATIVE HEALTH EDUC BLDG | C311 | Flat Floor Classroom | 30 | 778 | 11 | 1813 | 14.954 | 25.9333 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C313 | Classroom | 20 | 375 | 11 | 900 | 15.4011 | 18.75 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C314 | Classroom | 12 | 307 | 11 | 488 | 10.2005 | 25.5833 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C315 | Classroom | 12 | 311 | 11 | 488 | 10.0693 | 25.9167 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C331 | Special Purpose Teaching | 4 | 97 | 11 | 163 | 10.7834 | 24.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C332 | Special Purpose Teaching | 4 | 97 | 11 | 163 | 10.7834 | 24.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C333 | Special Purpose Teaching | 4 | 101 | 11 | 163 | 10.3563 | 25.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C335 | Special Purpose Teaching | 4 | 101 | 11 | 163 | 10.3563 | 25.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C336 | Special Purpose Teaching | 4 | 101 | 11 | 163 | 10.3563 | 25.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C341 | Special Purpose Teaching | 4 | 97 | 11 | 163 | 10.7834 | 24.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C342 | Special Purpose Teaching | 4 | 101 | 11 | 163 | 10.3563 | 25.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C343 | Special Purpose Teaching | 4 | 97 | 11 | 163 | 10.7834 | 24.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C345 | Special Purpose Teaching | 4 | 101 | 11 | 163 | 10.3563 | 25.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C346 | Special Purpose Teaching | 4 | 105 | 11 | 163 | 9.9618 | 26.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C351 | Special Purpose Teaching | 6 | 144 | 11 | 238 | 10.6061 | 24 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C352 | Special Purpose Teaching | 6 | 148 | 11 | 238 | 10.3194 | 24.6667 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C353 | Special Purpose Teaching | 6 | 144 | 11 | 238 | 10.6061 | 24 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C355 | Special Purpose Teaching | 6 | 148 | 11 | 238 | 10.3194 | 24.6667 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C356 | Special Purpose Teaching | 6 | 157 | 11 | 238 | 9.7279 | 26.1667 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C361 | Special Purpose Teaching | 6 | 137 | 11 | 238 | 11.148 | 22.8333 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C362 | Special Purpose Teaching | 6 | 138 | 11 | 238 | 11.0672 | 23 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C363 | Special Purpose Teaching | 6 | 135 | 11 | 363 | 17.2549 | 22.5 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C365 | Special Purpose Teaching | 6 | 137 | 11 | 313 | 14.661 | 22.8333 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C366 | Special Purpose Teaching | 6 | 137 | 11 | 238 | 11.148 | 22.8333 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C371 | Special Purpose Teaching | 18 | 965 | 11 | 988 | 6.5701 | 53.6111 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C371A | Special Purpose Teaching | 3 | 98 | 11 | 150 | 9.8221 | 32.6667 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C371B | Special Purpose Teaching | 3 | 100 | 11 | 150 | 9.6257 | 33.3333 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C373 | Special Purpose Teaching | 18 | 922 | 11 | 688 | 4.7885 | 51.2222 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C373A | Special Purpose Teaching | 3 | 100 | 11 | 150 | 9.6257 | 33.3333 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C373B | Special Purpose Teaching | 3 | 99 | 11 | 150 | 9.7229 | 33 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C376 | Special Purpose Teaching | 24 | 980 | 11 | 750 | 4.9111 | 40.8333 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
COLLABORATIVE HEALTH EDUC BLDG | C381 | Special Purpose Teaching | 20 | 503 | 11 | 925 | 11.8009 | 25.15 | Standard | Standard | Verified - HVAC design drawings (100 % OA capable)
DENTISTRY | 1200 | Flat Floor Classroom | 50 | 1418 | 9.75 | 1480 | 7.5564 | 28.36 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 1205 | Flat Floor Classroom | 25 | 593 | 9.33 | 620 | 7.9102 | 23.72 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 1206 | Flat Floor Classroom | 29 | 597 | 9.17 | 620 | 7.9943 | 20.5862 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 1303 | Classroom | 10 | 264 | 9 | 270 | 8.0214 | 26.4 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 1420 | Classroom | 14 | 342 | 8.92 | 355 | 8.2143 | 24.4286 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 2005 | Classroom | 12 | 286 | 7.83 | 413 | 13.0183 | 23.8333 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 2006 | LM COMPUTER LAB | 16 | 356 | 7.75 | 717 | 18.3442 | 22.25 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 2428 | Classroom | 12 | 242 | 8.4 | 255 | 8.8548 | 20.1667 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 2537 | Classroom | 22 | 387 | 9.4 | 400 | 7.7616 | 17.5909 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 3156 | Tiered /Fixed Classroom | 157 | 860 | 11.75 | 3207 | 22.4024 | 5.4777 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 3157 | Tiered /Fixed Classroom | 68 | 829 | 11.75 | 2883 | 20.8922 | 12.1912 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 3218 | Special Purpose Teaching | 56 | 2816 | 9.92 | 2800 | 7.0753 | 50.2857 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 3220 | Special Purpose Teaching | 52 | 2556 | 9.92 | 2800 | 7.795 | 49.1538 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 4110 | Classroom | 14 | 334 | 9 | 392 | 9.2051 | 23.8571 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 4111 | Classroom | 14 | 327 | 9 | 374 | 8.9704 | 23.3571 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 4112 | Classroom | 14 | 399 | 9 | 376 | 7.391 | 28.5 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 4113 | Classroom | 13 | 307 | 9 | 359 | 9.1716 | 23.6154 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 4114 | Classroom | 15 | 312 | 9 | 394 | 9.9045 | 20.8 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 4116 | Flat Floor Classroom | 80 | 1299 | 8.42 | 1355 | 8.7448 | 16.2375 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 4117 | Tiered /Fixed Classroom | 57 | 1095 | 8.42 | 2562 | 19.6149 | 19.2105 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 4258 | Special Purpose Teaching | 8 | 207 | 9.75 | 764 | 26.7209 | 25.875 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 5150 | Classroom | 22 | 425 | 8.92 | 632 | 11.7678 | 19.3182 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 5158 | Classroom | 17 | 349 | 7.83 | 473 | 12.2182 | 20.5294 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 5199 | Classroom | 15 | 354 | 8 | 355 | 8.8485 | 23.6 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 5214 | Classroom | 12 | 306 | 9 | 351 | 8.9965 | 25.5 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 5228 | Classroom | 20 | 334 | 8.02 | 388 | 10.2245 | 16.7 | Standard | Standard | Verified - HVAC design drawings
DENTISTRY | 5236 | Classroom | 14 | 447 | 9 | 411 | 7.2115 | 31.9286 | Standard | Standard | Verified - HVAC design drawings
FORREST | G07 | Classroom | 13 | 229 | 8.5 | 300 | 10.8793 | 17.6154 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
FORREST | G09 | Classroom | 11 | 205 | 8.5 | 212 | 8.5881 | 18.6364 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
FORREST | G38 | Classroom | 10 | 269 | 8.5 | 0 | 0 | 26.9 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | G54 | Classroom | 12 | 258 | 8.5 | 180 | 5.7938 | 21.5 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
FORREST | G55 | Classroom | 18 | 391 | 8.5 | 200 | 4.2478 | 21.7222 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
FORREST | 112 | Classroom | 20 | 314 | 14 | 0 | 0 | 15.7 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 147 | Special Purpose Teaching | 50 | 291 | 14 | 0 | 0 | 5.82 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 201 | Classroom | 13 | 262 | 14 | 0 | 0 | 20.1538 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 201A | Special Purpose Teaching | 12 | 967 | 14 | 0 | 0 | 80.5833 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 213 | Special Purpose Teaching | 70 | 1692 | 16 | 0 | 0 | 24.1714 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 218 | Classroom | 11 | 260 | 14 | 0 | 0 | 23.6364 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 219 | Special Purpose Teaching | 70 | 1505 | 14 | 0 | 0 | 21.5 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 309 | Special Purpose Teaching | 80 | 2559 | 13.5 | 0 | 0 | 31.9875 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 415 | Special Purpose Teaching | 60 | 2448 | 12 | 0 | 0 | 40.8 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 421 | Classroom | 18 | 330 | 12 | 0 | 0 | 18.3333 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
FORREST | 425 | Classroom | 12 | 203 | 12 | 64 | 1.8545 | 16.9167 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC Improvements)
LSRI-NORTH TOWER | N221 | Classroom | 10 | 449 | 9 | 570 | 9.9568 | 44.9 | Standard | Standard | Verified - HVAC design drawings
LSRI-NORTH TOWER | N303 | Classroom | 24 | 828 | 9 | 1290 | 12.2194 | 34.5 | Standard | Standard | Verified - HVAC design drawings
LSRI-NORTH TOWER | N406 | Classroom | 12 | 366 | 9 | 400 | 8.5717 | 30.5 | Standard | Standard | Verified - HVAC design drawings
LSRI-SOUTH TOWER | S207B | Classroom | 10 | 307 | 9 | 355 | 9.0694 | 30.7 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | 11B01 | Special Purpose Teaching | 12 | 352 | 9 | 410 | 9.1355 | 29.3333 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 12K01 | Special Purpose Teaching | 97 | 3689 | 9 | 5360 | 11.3958 | 38.0309 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 13A01 | Special Purpose Teaching | 12 | 400 | 9 | 520 | 10.1961 | 33.3333 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 14B02 | Flat Floor Classroom | 30 | 939 | 9 | 1112 | 9.2881 | 31.3 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 14F01 | Special Purpose Teaching | 40 | 1073 | 9 | 1424 | 10.4088 | 26.825 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 14G01 | Special Purpose Teaching | 115 | 3528 | 9 | 3916 | 8.7057 | 30.6783 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 2A12 | Classroom | 8 | 280 | 9 | 215 | 6.0224 | 35 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 2B08 | Special Purpose Teaching | 15 | 780 | 9 | 810 | 8.1448 | 52 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 3A01 | Classroom | 15 | 408 | 9 | 490 | 9.4195 | 27.2 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 3H01 | Tiered /Fixed Classroom | 92 | 1007 | 9.92 | 1296 | 9.1579 | 10.9457 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 3L01 | Special Purpose Teaching | 45 | 1077 | 9 | 1589 | 11.5717 | 23.9333 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 4N01 | Special Purpose Teaching | 12 | 390 | 9 | 460 | 9.2509 | 32.5 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 6B01 | Special Purpose Teaching | 12 | 267 | 9 | 250 | 7.3438 | 22.25 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 6L01 | Special Purpose Teaching | 40 | 920 | 9 | 1200 | 10.2302 | 23 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 6M01 | Classroom | 10 | 280 | 9 | 200 | 5.6022 | 28 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 7C03 | Special Purpose Teaching | 10 | 405 | 9 | 500 | 9.6829 | 40.5 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 8J01 | Special Purpose Teaching | 60 | 3533 | 9 | 4875 | 10.8223 | 58.8833 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 9A01 | Special Purpose Teaching | 20 | 298 | 9 | 350 | 9.2117 | 14.9 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | 9A02 | Special Purpose Teaching | 16 | 290 | 9 | 350 | 9.4659 | 18.125 | Standard | Standard | Verified - HVAC design drawings (100 % OA)
TUPPER BLDG | BA3 | Special Purpose Teaching | 12 | 568 | 9 | 900 | 12.4275 | 47.3333 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | G36 | Classroom | 15 | 424 | 9 | 1060 | 19.6078 | 28.2667 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L10 | Flat Floor Classroom | 45 | 691 | 9 | 960 | 10.8964 | 15.3556 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L11 | Classroom | 10 | 283 | 8 | 350 | 10.9125 | 28.3 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L12 | Classroom | 10 | 235 | 9 | 420 | 14.0175 | 23.5 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L13 | Classroom | 10 | 283 | 8 | 350 | 10.9125 | 28.3 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L14 | Classroom | 10 | 237 | 9 | 420 | 13.8992 | 23.7 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L15 | Classroom | 10 | 283 | 8.92 | 350 | 9.787 | 28.3 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L16 | Classroom | 10 | 213 | 9 | 420 | 15.4653 | 21.3 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L17 | Classroom | 10 | 279 | 8.92 | 350 | 9.9273 | 27.9 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L18 | Classroom | 10 | 235 | 9 | 420 | 14.0175 | 23.5 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L21 | Classroom | 10 | 221 | 8.92 | 260 | 9.31 | 22.1 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L24 | Classroom | 10 | 216 | 8.92 | 270 | 9.8918 | 21.6 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L25 | Special Purpose Teaching | 10 | 272 | 8.92 | 360 | 10.4737 | 27.2 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L3 | Special Purpose Teaching | 24 | 506 | 8.92 | 935 | 14.6227 | 21.0833 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | L7 | Flat Floor Classroom | 28 | 600 | 8.5 | 700 | 9.6886 | 21.4286 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | THTR A | Tiered /Fixed Classroom | 120 | 2008 | 11.25 | 4300 | 13.4365 | 16.7333 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | THTR B | Tiered /Fixed Classroom | 189 | 2108 | 11.5 | 4300 | 12.5208 | 11.1534 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | THTR C | Tiered /Fixed Classroom | 97 | 1008 | 10 | 2200 | 15.4062 | 10.3918 | Standard | Standard | Verified - HVAC design drawings
TUPPER BLDG | THTR D | Tiered /Fixed Classroom | 105 | 795 | 10.83 | 1600 | 13.1177 | 7.5714 | Standard | Standard | Verified - HVAC design drawings
Assumptions & Notes:
1) List of learning spaces provided by FM Space management team
2) Pre-COVID room capacities were collected from Campus Space Database
3) Room area data collected from Campus Space Database
4) Room height data collected physically using a laser measure
5) All Air Flow (CFM) measurements are total air flow supplied to the room (fresh air + recirculated filtered air)
6) Standard air flow is considered as total flow of 3 ACH or greater.
7) To calculate the functional volume of a classroom, 15% was deducted from each room for dead space (furniture, equipment, built-ins, people,etc)
8) Original HVAC assessment included assessing the capabilities of the ventilation systems at the building level.

## Studley
Classroom HVAC Master Sheet - Studley Campus (updated August 12th)
Building Name | Room Number | Room Type | Pre-COVID Capacity | Area (sq.ft) | Room Height (ft) | Air Flow (CFM) | Air Changes per Hr (ACH) | Ocuppant Density | Original HVAC Assessment | Post Verification Assessment | Source of Air Volume Data
DALPLEX | 206 | Classroom | 25 | 980 | 12 | 740 | 4.4418 | 39.2 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
DALPLEX | 223 | Classroom | 25 | 579 | 11.5 | 580 | 6.1487 | 23.16 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
LSC-BIOL&EARTH | B2012 | Computer Lab | 20 | 1010 | 11 | 1500 | 9.5304 | 50.5 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2020A | Special Purpose Teaching | 20 | 792 | 11 | 1400 | 11.3434 | 39.6 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2020B | Classroom | 6 | 323 | 11 | 350 | 6.9535 | 53.8333 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2030 | Special Purpose Teaching | 24 | 784 | 11 | 1400 | 11.4591 | 32.6667 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2055 | Special Purpose Teaching | 48 | 1885 | 11 | 1800 | 6.1277 | 39.2708 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2084 | Computer Lab | 11 | 383 | 11 | 600 | 10.0529 | 34.8182 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2087 | Computer Lab | 30 | 690 | 11 | 900 | 8.3701 | 23 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2097 | Special Purpose Teaching | 30 | 1378 | 11 | 1500 | 6.9852 | 45.9333 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2098 | Special Purpose Teaching | 30 | 1006 | 11 | 1500 | 9.5683 | 33.5333 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2100 | Special Purpose Teaching | 30 | 1343 | 11 | 1500 | 7.1673 | 44.7667 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2102 | Special Purpose Teaching | 44 | 1749 | 11 | 1200 | 4.4028 | 39.75 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2109 | Special Purpose Teaching | 12 | 715 | 11 | 900 | 8.0775 | 59.5833 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B2112 | Special Purpose Teaching | 24 | 864 | 11 | 900 | 6.6845 | 36 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B4009 | Special Purpose Teaching | 24 | 986 | 11 | 1200 | 7.8099 | 41.0833 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
LSC-BIOL&EARTH | B4012 | Special Purpose Teaching | 30 | 983 | 11 | 1200 | 7.8337 | 32.7667 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
LSC-BIOL&EARTH | B4016 | Special Purpose Teaching | 28 | 1075 | 11 | 1200 | 7.1633 | 38.3929 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
LSC-BIOL&EARTH | B4082 | Classroom | 10 | 316 | 11 | 450 | 9.1383 | 31.6 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
LSC-BIOL&EARTH | B5009 | Special Purpose Teaching | 24 | 988 | 11 | 1200 | 7.7941 | 41.1667 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
LSC-BIOL&EARTH | B5012 | Special Purpose Teaching | 24 | 983 | 11 | 900 | 5.8753 | 40.9583 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
LSC-BIOL&EARTH | B6009 | Special Purpose Teaching | 24 | 992 | 11 | 1200 | 7.7626 | 41.3333 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
LSC-BIOL&EARTH | B6012 | Computer Lab | 24 | 985 | 11 | 1800 | 11.7267 | 41.0417 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
LSC-BIOL&EARTH | B7009 | Special Purpose Teaching | 24 | 986 | 11 | 800 | 5.2066 | 41.0833 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B7012 | Special Purpose Teaching | 24 | 995 | 11 | 895 | 5.7722 | 41.4583 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B7123 | Classroom | 10 | 306 | 11 | 260 | 5.4524 | 30.6 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B8007 | Flat Floor Classroom | 34 | 831 | 11 | 2536 | 19.5834 | 24.4412 | Standard | Standard | Verified - HVAC design drawings
LSC-BIOL&EARTH | B812 | Classroom | 30 | 662 | 11 | 1000 | 9.6935 | 22.0667 | Standard | Standard | Verified - HVAC design drawings
LSC-OCEANOGRAPH | O2660 | Special Purpose Teaching | 48 | 2253 | 11 | 1815 | 5.1696 | 46.9375 | Standard | Standard | Verified - HVAC design drawings
LSC-OCEANOGRAPH | O3652 | Flat Floor Classroom | 35 | 652 | 8 | 1500 | 20.2995 | 18.6286 | Standard | Standard | Verified - HVAC design drawings
LSC-OCEANOGRAPH | O3655 | Flat Floor Classroom | 40 | 918 | 11 | 1020 | 7.1301 | 22.95 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P4207 | Computer Lab | 22 | 565 | 11 | 990 | 11.2441 | 25.6818 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P4208 | Classroom | 23 | 523 | 11 | 990 | 12.1471 | 22.7391 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P4212 | Classroom | 12 | 185 | 11 | 350 | 12.1405 | 15.4167 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P4245 | Special Purpose Teaching | 12 | 593 | 11 | 850 | 9.1982 | 49.4167 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P4260 | Tiered /Fixed Classroom | 116 | 1717 | 8.5 | 3100 | 14.9936 | 14.8017 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P4269 | Classroom | 12 | 341 | 11 | 530 | 9.9738 | 28.4167 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P4310 | Classroom | 12 | 167 | 11 | 1100 | 42.2684 | 13.9167 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P5207 | Special Purpose Teaching | 34 | 556 | 11 | 1100 | 12.6957 | 16.3529 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P5208 | Classroom | 25 | 532 | 11 | 1100 | 13.2685 | 21.28 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P5257 | Special Purpose Teaching | 20 | 535 | 11 | 640 | 7.6765 | 26.75 | Standard | Standard | Verified - HVAC design drawings
LSC-PSYCHOLOGY | P5260 | Tiered /Fixed Classroom | 120 | 801 | 8.5 | 1770 | 18.3508 | 6.675 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C202 | Flat Floor Classroom | 40 | 580 | 11 | 800 | 8.8512 | 14.5 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C206 | Flat Floor Classroom | 60 | 764 | 11 | 1125 | 9.4493 | 12.7333 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C208 | Flat Floor Classroom | 54 | 756 | 11 | 1125 | 9.5493 | 14 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C210 | Classroom | 20 | 362 | 11 | 375 | 6.6476 | 18.1 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C212 | Classroom | 23 | 362 | 11 | 375 | 6.6476 | 15.7391 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C214 | Classroom | 22 | 344 | 11 | 375 | 6.9954 | 15.6364 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C216 | Flat Floor Classroom | 40 | 592 | 11 | 875 | 9.4848 | 14.8 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C220 | Flat Floor Classroom | 35 | 960 | 11 | 1500 | 10.0267 | 27.4286 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C222 | Special Purpose Teaching | 25 | 589 | 11 | 875 | 9.5331 | 23.56 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C234 | Flat Floor Classroom | 44 | 690 | 11 | 1000 | 9.3002 | 15.6818 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C236 | Tiered /Fixed Classroom | 119 | 1760 | 14 | 2100 | 6.016 | 14.7899 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C238 | Tiered /Fixed Classroom | 80 | 1184 | 10.25 | 1600 | 9.3063 | 14.8 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C240 | Tiered /Fixed Classroom | 123 | 1824 | 12.25 | 1500 | 4.7387 | 14.8293 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C242 | Tiered /Fixed Classroom | 149 | 1781 | 12.25 | 1500 | 4.8531 | 11.953 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C244 | Flat Floor Classroom | 50 | 797 | 11 | 1200 | 9.6619 | 15.94 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C332 | Flat Floor Classroom | 70 | 939 | 11.67 | 1400 | 9.0183 | 13.4143 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C334 | Flat Floor Classroom | 53 | 690 | 11.67 | 1000 | 8.7662 | 13.0189 | Standard | Standard | Verified - HVAC design drawings
LSC-COMMON AREA | C338 | Tiered /Fixed Classroom | 64 | 1187 | 13 | 1650 | 7.5478 | 18.5469 | Standard | Standard | Verified - HVAC design drawings
SIR JAMES DUNN | 101 | Tiered /Fixed Classroom | 82 | 1230 | 12 | 1996 | 9.5457 | 15 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 107 | Special Purpose Teaching | 21 | 860 | 13 | 1132 | 7.1472 | 40.9524 | Standard | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 114 | Special Purpose Teaching | 51 | 1446 | 13 | 989 | 3.7138 | 28.3529 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 117 | Tiered /Fixed Classroom | 234 | 3118 | 16 | 3900 | 5.5182 | 13.3248 | Measurement & Verification Required | Standard | Verified - HVAC Design drawings - could not access all the supply grills to measure
SIR JAMES DUNN | 135 | Tiered /Fixed Classroom | 82 | 1053 | 11.5 | 2026 | 11.8099 | 12.8415 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 201 | Special Purpose Teaching | 30 | 1660 | 11 | 2466 | 9.5329 | 55.3333 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 208 | Computer Lab | 23 | 605 | 11 | 0 | 0 | 26.3043 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC improvements)
SIR JAMES DUNN | 221C | Flat Floor Classroom | 35 | 860 | 11 | 260 | 1.9401 | 24.5714 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC improvements)
SIR JAMES DUNN | 221E | Special Purpose Teaching | 30 | 728 | 11 | 657 | 5.7913 | 24.2667 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 245A | Classroom | 24 | 215 | 11 | 150 | 4.4771 | 8.9583 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 301A | Computer Lab | 64 | 1793 | 11 | 1620 | 5.7979 | 28.0156 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 301B | Computer Lab | 70 | 2082 | 11 | 1723 | 5.3106 | 29.7429 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 302 | Flat Floor Classroom | 45 | 958 | 11 | 700 | 4.6889 | 21.2889 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
SIR JAMES DUNN | 304 | Tiered /Fixed Classroom | 60 | 1242 | 11 | 1347 | 6.9596 | 20.7 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CHASE BLDG | 107 | Classroom | 5 | 192 | 9 | 0 | 0 | 38.4 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC improvements)
CHASE BLDG | 227 | Classroom | 17 | 370 | 14 | 1600 | 21.8033 | 21.7647 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CHASE BLDG | 319 | Flat Floor Classroom | 36 | 1231 | 14 | 0 | 0 | 34.1944 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC improvements)
HENRY HICKS ACADEMIC | 212 | Tiered /Fixed Classroom | 110 | 1110 | 12 | 0 | 0 | 10.0909 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC improvements)
HENRY HICKS ACADEMIC | 217 | Tiered /Fixed Classroom | 73 | 1073 | 12 | 0 | 0 | 14.6986 | Measurement & Verification Required | Sub Standard | Measured & Verified - In-house HVAC technicians (requires HVAC improvements)
CHEMISTRY | 125 | Tiered /Fixed Classroom | 167 | 1537 | 16 | 1216 | 3.4904 | 9.2036 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians (100 % fresh air)
CHEMISTRY | 223 | Flat Floor Classroom | 50 | 633 | 10 | 978 | 10.906 | 12.66 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CHEMISTRY | 226 | Tiered /Fixed Classroom | 114 | 1065 | 10 | 1456 | 9.6504 | 9.3421 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CHEMISTRY | 540 | Flat Floor Classroom | 28 | 767 | 10 | 650 | 5.9821 | 27.3929 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
CHEMISTRY PODIUM | 100 | Special Purpose Teaching | 60 | 2832 | 9 | 4701.12 | 13.0196 | 47.2 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
CHEMISTRY PODIUM | 108 | Special Purpose Teaching | 60 | 3187 | 9 | 5290.42 | 13.0196 | 53.1167 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
CHEMISTRY PODIUM | 111 | Special Purpose Teaching | 30 | 1915 | 9 | 3178.9 | 13.0196 | 63.8333 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
CHEMISTRY PODIUM | 115 | Special Purpose Teaching | 30 | 1520 | 9 | 2523.2 | 13.0196 | 50.6667 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
CHEMISTRY PODIUM | 118 | Special Purpose Teaching | 35 | 1918 | 9 | 3183.88 | 13.0196 | 54.8 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
CHEMISTRY PODIUM | 121 | Special Purpose Teaching | 30 | 2420 | 9 | 4017.2 | 13.0196 | 80.6667 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
CHEMISTRY PODIUM | 125 | Special Purpose Teaching | 30 | 2238 | 9 | 3715.08 | 13.0196 | 74.6 | Standard | Standard | Verified - HVAC Design drawings (100 % OA)
KILLAM LIBRARY | G42 | Classroom | 1 | 196 | 8.5 | 141 | 5.9742 | 196 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
KILLAM LIBRARY | G70 | Computer Lab | 1 | 664 | 8.5 | 765 | 9.5677 | 664 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
KILLAM LIBRARY | MACME | Tiered /Fixed Classroom | 230 | 2757 | 12 | 2424 | 5.1719 | 11.987 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
KILLAM LIBRARY | 2600 | Special Purpose Teaching | 115 | 3280 | 11 | 4629 | 9.0563 | 28.5217 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
KILLAM LIBRARY | 2616 | Tiered /Fixed Classroom | 54 | 947 | 17 | 1432 | 6.2788 | 17.537 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
KILLAM LIBRARY | 2622 | Flat Floor Classroom | 32 | 1127 | 11 | 1194 | 6.7986 | 35.2188 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
KILLAM LIBRARY | 4106 | Flat Floor Classroom | 40 | 617 | 11 | 567 | 5.8971 | 15.425 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
LEMARCHANT PLACE | 2303 | Classroom | 6 | 209 | 9 | 265 | 9.9446 | 34.8333 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 1107 | Flat Floor Classroom | 32 | 923 | 9 | 1200 | 10.1969 | 28.8438 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 1108 | Flat Floor Classroom | 64 | 1470 | 9 | 1600 | 8.5367 | 22.9688 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 1110 | Classroom | 30 | 737 | 9 | 800 | 8.5136 | 24.5667 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 1111 | Flat Floor Classroom | 32 | 770 | 9 | 1000 | 10.1859 | 24.0625 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 1201 | Special Purpose Teaching | 58 | 1756 | 9 | 2340 | 10.4516 | 30.2759 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 2010 | Classroom | 8 | 198 | 9 | 200 | 7.9224 | 24.75 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 2019 | Classroom | 8 | 176 | 9 | 200 | 8.9127 | 22 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 2107 | Flat Floor Classroom | 40 | 930 | 9 | 1400 | 11.8069 | 23.25 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 2108 | Special Purpose Teaching | 12 | 488 | 9 | 1100 | 17.6792 | 40.6667 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 2109 | Special Purpose Teaching | 16 | 679 | 9 | 1660 | 19.1747 | 42.4375 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 2110 | Classroom | 20 | 473 | 9 | 600 | 9.949 | 23.65 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 2111 | Flat Floor Classroom | 40 | 930 | 9 | 1200 | 10.1202 | 23.25 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 3011 | Classroom | 8 | 177 | 9 | 200 | 8.8623 | 22.125 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 3107 | Tiered /Fixed Classroom | 45 | 930 | 9 | 1200 | 10.1202 | 20.6667 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 3109 | Flat Floor Classroom | 40 | 954 | 9 | 1500 | 12.332 | 23.85 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 3110 | Classroom | 20 | 473 | 9 | 600 | 9.949 | 23.65 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 3111 | Flat Floor Classroom | 34 | 930 | 9 | 1300 | 10.9635 | 27.3529 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 4006 | Classroom | 8 | 289 | 9 | 750 | 20.3542 | 36.125 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 4013 | Classroom | 8 | 202 | 9 | 450 | 17.4723 | 25.25 | Standard | Standard | Verified - HVAC design drawings
MONA CAMPBELL BUILDING | 4023 | Classroom | 8 | 289 | 9 | 700 | 18.9972 | 36.125 | Standard | Standard | Verified - HVAC design drawings
ARTS CENTRE | 5 | Special Purpose Teaching | 4 | 112 | 7.75 | 240 | 19.5175 | 28 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 104 | Special Purpose Teaching | 10 | 220 | 15.83 | 300 | 6.0806 | 22 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 106 | Special Purpose Teaching | 8 | 287 | 9.42 | 300 | 7.8329 | 35.875 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 111 | Special Purpose Teaching | 35 | 758 | 10.5 | 600 | 5.3214 | 21.6571 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 113 | Special Purpose Teaching | 3 | 115 | 12 | 80 | 4.0921 | 38.3333 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 114 | Special Purpose Teaching | 4 | 168 | 12.92 | 240 | 7.805 | 42 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 121 | Special Purpose Teaching | 96 | 2354 | 18 | 2400 | 3.9982 | 24.5208 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 163 | Special Purpose Teaching | 90 | 2100 | 18 | 1800 | 3.3613 | 23.3333 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201A | Special Purpose Teaching | 2 | 46 | 7.58 | 80 | 16.1955 | 23 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201B | Special Purpose Teaching | 2 | 60 | 7.25 | 80 | 12.9817 | 30 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201C | Special Purpose Teaching | 2 | 81 | 7.58 | 80 | 9.1975 | 40.5 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201D | Special Purpose Teaching | 2 | 60 | 7.25 | 80 | 12.9817 | 30 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201E | Special Purpose Teaching | 4 | 102 | 7.5 | 120 | 11.0727 | 25.5 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201F | Special Purpose Teaching | 2 | 56 | 7.58 | 80 | 13.3035 | 28 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201G | Special Purpose Teaching | 2 | 56 | 7.75 | 80 | 13.0117 | 28 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201H | Special Purpose Teaching | 2 | 56 | 7.75 | 80 | 13.0117 | 28 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201I | Special Purpose Teaching | 2 | 56 | 7.58 | 80 | 13.3035 | 28 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201J | Special Purpose Teaching | 2 | 56 | 7.58 | 80 | 13.3035 | 28 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201K | Special Purpose Teaching | 2 | 56 | 7.75 | 80 | 13.0117 | 28 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201L | Special Purpose Teaching | 2 | 72 | 7.4 | 80 | 10.5988 | 36 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201M | Special Purpose Teaching | 4 | 111 | 7.75 | 120 | 9.8467 | 27.75 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201N | Special Purpose Teaching | 12 | 474 | 7 | 400 | 8.5097 | 39.5 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201O | Special Purpose Teaching | 2 | 48 | 7.75 | 80 | 15.1803 | 24 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201P | Special Purpose Teaching | 2 | 56 | 7.75 | 80 | 13.0117 | 28 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201Q | Special Purpose Teaching | 2 | 53 | 7.75 | 80 | 13.7482 | 26.5 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 201R | Special Purpose Teaching | 2 | 48 | 7.75 | 80 | 15.1803 | 24 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 215 | Computer Lab | 10 | 525 | 8 | 600 | 10.084 | 52.5 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 326 | Special Purpose Teaching | 12 | 340 | 10 | 360 | 7.474 | 28.3333 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 327 | Special Purpose Teaching | 70 | 1576 | 18 | 1800 | 4.4789 | 22.5143 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 329 (Dunn) | Special Purpose Teaching | 198 | 3042 | 37 | 24000 | 15.0516 | 15.3636 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 406 | Special Purpose Teaching | 90 | 1431 | 17.92 | 2400 | 6.6064 | 15.9 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 407 | Special Purpose Teaching | 5 | 219 | 8.1 | 480 | 19.1005 | 43.8 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 408 | Classroom | 12 | 219 | 9.17 | 480 | 16.8717 | 18.25 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 409 | Flat Floor Classroom | 40 | 800 | 7.5 | 600 | 7.0588 | 20 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 534 | Special Purpose Teaching | 14 | 720 | 8 | 800 | 9.8039 | 51.4286 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 513C | Special Purpose Teaching | 4 | 162 | 7.5 | 700 | 40.6681 | 40.5 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
ARTS CENTRE | 533A | Classroom | 12 | 161 | 8 | 600 | 32.8827 | 13.4167 | Measurement & Verification Required | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | AUD-1 | Tiered /Fixed Classroom | 256 | 4312 | 20 | 10000 | 8.1851 | 16.8438 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | AUD-2 | Tiered /Fixed Classroom | 495 | 4856 | 20 | 15000 | 10.9022 | 9.8101 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 1102 | Flat Floor Classroom | 36 | 755 | 9.5 | 1300 | 12.794 | 20.9722 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 1116 | Flat Floor Classroom | 36 | 783 | 9.5 | 1300 | 12.3365 | 21.75 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 1130 | Flat Floor Classroom | 36 | 783 | 9.5 | 1300 | 12.3365 | 21.75 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 1170 | Flat Floor Classroom | 36 | 783 | 9.5 | 1300 | 12.3365 | 21.75 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 1184 | Flat Floor Classroom | 26 | 783 | 9.5 | 1300 | 12.3365 | 30.1154 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 1198 | Flat Floor Classroom | 36 | 755 | 9.5 | 1300 | 12.794 | 20.9722 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2016 | Flat Floor Classroom | 36 | 803 | 9.5 | 1300 | 12.0292 | 22.3056 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2017 | Flat Floor Classroom | 36 | 811 | 9.5 | 1300 | 11.9105 | 22.5278 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2018 | Special Purpose Teaching | 26 | 811 | 9.5 | 1300 | 11.9105 | 31.1923 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2019 | Computer Lab | 52 | 1589 | 9.5 | 2600 | 12.1579 | 30.5577 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2020 | Computer Lab | 15 | 811 | 9.5 | 1300 | 11.9105 | 54.0667 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2021 | Flat Floor Classroom | 36 | 811 | 9.5 | 1300 | 11.9105 | 22.5278 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2022 | Special Purpose Teaching | 26 | 803 | 9.5 | 1300 | 12.0292 | 30.8846 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2102 | Flat Floor Classroom | 36 | 753 | 9.5 | 1300 | 12.8279 | 20.9167 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2104 | Computer Lab | 32 | 805 | 9.5 | 1300 | 11.9993 | 25.1562 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2116 | Flat Floor Classroom | 36 | 780 | 9.5 | 1300 | 12.3839 | 21.6667 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2118 | Flat Floor Classroom | 36 | 797 | 9.5 | 1300 | 12.1198 | 22.1389 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2130 | Flat Floor Classroom | 36 | 780 | 9.5 | 1300 | 12.3839 | 21.6667 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2132 | Flat Floor Classroom | 36 | 805 | 9.5 | 1300 | 11.9993 | 22.3611 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2162 | Flat Floor Classroom | 36 | 805 | 9.5 | 1300 | 11.9993 | 22.3611 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2170 | Flat Floor Classroom | 36 | 780 | 9.5 | 1300 | 12.3839 | 21.6667 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2176 | Flat Floor Classroom | 36 | 806 | 9.5 | 1300 | 11.9844 | 22.3889 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2184 | Flat Floor Classroom | 36 | 780 | 9.5 | 1300 | 12.3839 | 21.6667 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2190 | Flat Floor Classroom | 36 | 806 | 9.5 | 1300 | 11.9844 | 22.3889 | Standard | Standard | Verified - HVAC design drawings
MCCAIN ARTS&SS | 2198 | Flat Floor Classroom | 36 | 753 | 9.5 | 1300 | 12.8279 | 20.9167 | Standard | Standard | Verified - HVAC design drawings
WELDON LAW | 104 | Tiered /Fixed Classroom | 87 | 1774 | 10 | 2841 | 11.3045 | 20.3908 | Standard | Standard | Measured & Verified - Matheson Air Balancing
WELDON LAW | 105 | Tiered /Fixed Classroom | 175 | 2889 | 10 | 3901 | 9.5315 | 16.5086 | Standard | Standard | Measured & Verified - Matheson Air Balancing
WELDON LAW | W204 | Tiered /Fixed Classroom | 55 | 1159 | 10 | 2016 | 12.2783 | 21.0727 | Standard | Standard | Measured & Verified - Matheson Air Balancing
WELDON LAW | W207 | Tiered /Fixed Classroom | 60 | 1281 | 10 | 1242 | 6.8439 | 21.35 | Standard | Standard | Measured & Verified - Matheson Air Balancing
WELDON LAW | W305 | Tiered /Fixed Classroom | 80 | 2454 | 10 | 1904 | 5.4768 | 30.675 | Standard | Standard | Measured & Verified - Matheson Air Balancing
WELDON LAW | W308 | Classroom | 22 | 568 | 9 | 809 | 11.1709 | 25.8182 | Standard | Standard | Measured & Verified - Matheson Air Balancing
WELDON LAW | W309 | Classroom | 20 | 568 | 9 | 442 | 6.1033 | 28.4 | Standard | Standard | Measured & Verified - Matheson Air Balancing
WELDON LAW | W411 | Classroom | 22 | 990 | 9 | 1715 | 13.5868 | 45 | Standard | Standard | Measured & Verified - Matheson Air Balancing
WELDON LAW | W448 | Special Purpose Teaching | 25 | 130 | 9 | 469 | 28.2956 | 5.2 | Standard | Standard | Measured & Verified - Matheson Air Balancing
KENNETH C ROWE MANAG | 1007 | Tiered /Fixed Classroom | 58 | 1130 | 10 | 1870 | 11.6814 | 19.4828 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 1009 | Tiered /Fixed Classroom | 80 | 1658 | 10 | 2138 | 9.1024 | 20.725 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 1011 | Tiered /Fixed Classroom | 80 | 1666 | 10 | 2110 | 8.94 | 20.825 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 1014 | Tiered /Fixed Classroom | 60 | 1192 | 10 | 1605 | 9.5045 | 19.8667 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 1016 | Tiered /Fixed Classroom | 60 | 1193 | 10 | 1652 | 9.7747 | 19.8833 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 1020 | Tiered /Fixed Classroom | 120 | 2582 | 10 | 3124 | 8.5406 | 21.5167 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 1028 | Tiered /Fixed Classroom | 390 | 4027 | 10 | 12000 | 21.0345 | 10.3256 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 2068 | Classroom | 22 | 734 | 8.5 | 1230 | 13.9163 | 33.3636 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 3001 | Flat Floor Classroom | 30 | 730 | 8.5 | 1400 | 15.9264 | 24.3333 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 3080 | Computer Lab | 30 | 760 | 8.5 | 1600 | 17.4832 | 25.3333 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 3081 | Classroom | 6 | 130 | 8.5 | 160 | 10.2209 | 21.6667 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 3082 | Classroom | 6 | 185 | 8.5 | 300 | 13.4668 | 30.8333 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 3085 | Classroom | 6 | 113 | 8.5 | 160 | 11.7586 | 18.8333 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 3087 | Special Purpose Teaching | 12 | 721 | 8.5 | 1380 | 15.8949 | 60.0833 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 3089 | Special Purpose Teaching | 50 | 1187 | 8.5 | 2400 | 16.7909 | 23.74 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 4001 | Computer Lab | 24 | 717 | 8.5 | 1400 | 16.2152 | 29.875 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 4055 | Computer Lab | 40 | 1550 | 8.5 | 3100 | 16.609 | 38.75 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 4061 | Classroom | 4 | 138 | 8.5 | 150 | 9.0266 | 34.5 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 4063 | Classroom | 4 | 174 | 8.5 | 190 | 9.0681 | 43.5 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 4095 | Classroom | 7 | 210 | 8.5 | 165 | 6.525 | 30 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 4125 | Classroom | 4 | 117 | 8.5 | 120 | 8.5174 | 29.25 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 4137 | Classroom | 6 | 172 | 8.5 | 340 | 16.4159 | 28.6667 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 5001 | Flat Floor Classroom | 30 | 730 | 8.5 | 1400 | 15.9264 | 24.3333 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 5053 | Flat Floor Classroom | 50 | 1174 | 8.5 | 1600 | 11.3179 | 23.48 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 5095 | Classroom | 7 | 138 | 8.5 | 160 | 9.6284 | 19.7143 | Standard | Standard | Verified - HVAC design drawings
KENNETH C ROWE MANAG | 5125 | Classroom | 4 | 143 | 8.5 | 160 | 9.2917 | 35.75 | Standard | Standard | Verified - HVAC design drawings
COMPUTER SCIENCE | 103 | Classroom | 15 | 325 | 10 | 393 | 8.5357 | 21.6667 | Standard | Standard | Measured & Verified - In-house HVAC technicians
COMPUTER SCIENCE | 127 | Tiered /Fixed Classroom | 120 | 1542 | 15 | 3900 | 11.902 | 12.85 | Standard | Standard | Verified - HVAC design drawings
COMPUTER SCIENCE | 134 | Special Purpose Teaching | 60 | 1486 | 9.5 | 1859 | 9.2954 | 24.7667 | Standard | Standard | Measured & Verified - In-house HVAC technicians
COMPUTER SCIENCE | 143 | Special Purpose Teaching | 64 | 1447 | 9.5 | 1824 | 9.3662 | 22.6094 | Standard | Standard | Measured & Verified - In-house HVAC technicians
COMPUTER SCIENCE | 211 | Classroom | 10 | 378 | 10 | 603 | 11.2605 | 37.8 | Standard | Standard | Measured & Verified - In-house HVAC technicians
COMPUTER SCIENCE | 228 | Special Purpose Teaching | 20 | 601 | 9.5 | 610 | 7.5416 | 30.05 | Standard | Standard | Measured & Verified - In-house HVAC technicians
COMPUTER SCIENCE | 311 | Classroom | 20 | 378 | 9.5 | 600 | 11.7942 | 18.9 | Standard | Standard | Verified - HVAC design drawings
COMPUTER SCIENCE | 330 | Computer Lab | 20 | 1096 | 9.5 | 1600 | 10.8472 | 54.8 | Standard | Standard | Verified - HVAC design drawings
COMPUTER SCIENCE | 429 | Classroom | 20 | 541 | 9.5 | 600 | 8.2407 | 27.05 | Standard | Standard | Verified - HVAC design drawings
COMPUTER SCIENCE | 430 | Flat Floor Classroom | 30 | 893 | 9.5 | 1600 | 13.313 | 29.7667 | Standard | Standard | Verified - HVAC design drawings
COMPUTER SCIENCE | 445 | Classroom | 8 | 169 | 9.5 | 300 | 13.19 | 21.125 | Standard | Standard | Verified - HVAC design drawings
Assumptions & Notes:
1) List of learning spaces provided by FM Space management team
2) Pre-COVID room capacities were collected from Campus Space Database
3) Room area data collected from Campus Space Database
4) Room height data collected physically using a laser measure
5) All Air Flow (CFM) measurements are total air flow supplied to the room (fresh air + recirculated filtered air)
6) Standard air flow is considered as total flow of 3 ACH or greater.
7) To calculate the functional volume of a classroom, 15% was deducted from each room for dead space (furniture, equipment, built-ins, people,etc)
8) Original HVAC assessment included assessing the capabilities of the ventilation systems at the building level.
Note on F38: Kyle MacKenzie: AVG Ceiling Height
Note on F44: Kyle MacKenzie: AVG Ceiling Height
Note on F55: Kyle MacKenzie: Average Ceiling height

## Sexton
Classroom HVAC Master Sheet - Sexton Campus (updated August 12th)
Building Name | Room Number | Room Type | Pre-COVID Capacity | Area (sq.ft) | Room Height (ft) | Air Flow (CFM) | Air Changes per Hr (ACH) | Ocuppant Density | Original HVAC Assessment | Post Verification Assessment | Source of Air Volume Data
A Building | A102 | Special Purpose Teaching | 28 | 652 | 9 | 150 | 1.8044 | 23.2857 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
A Building | A103 | Special Purpose Teaching | 15 | 1226 | 9 | 1299 | 8.3101 | 81.7333 | Standard | Standard | Measured & Verified - Matheson Air Balancing
A Building | A201 | Computer Lab | 40 | 992 | 11 | 0 | 0 | 24.8 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
A Building | A222 | Computer Lab | 30 | 918 | 9.5 | 0 | 0 | 30.6 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
B Building | B099 | Special Purpose Teaching | 12 | 1211 | 12 | 0 | 0 | 100.9167 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
B Building | B225 | Flat Floor Classroom | 200 | 1657 | 11 | 2546 | 9.86 | 8.285 | Standard | Standard | Measured & Verified - Matheson Air Balancing
B Building | B226 | Tiered /Fixed Classroom | 64 | 1061 | 11 | 449 | 2.7156 | 16.5781 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
B Building | B227 | Tiered /Fixed Classroom | 64 | 1061 | 11 | 378 | 2.2862 | 16.5781 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
B Building | B228 | Tiered /Fixed Classroom | 60 | 1002 | 11 | 348 | 2.2287 | 16.7 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
B Building | B229 | Tiered /Fixed Classroom | 64 | 1060 | 11 | 114 | 0.69014 | 16.5625 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
B Building | B233A | Special Purpose Teaching | 24 | 1314 | 11 | 906 | 4.4246 | 54.75 | Standard | Standard | Measured & Verified - Matheson Air Balancing
B Building | B308 | Tiered /Fixed Classroom | 125 | 1062 | 11 | 1020 | 6.1633 | 8.496 | Standard | Standard | Measured & Verified - Matheson Air Balancing
B Building | B310 | Tiered /Fixed Classroom | 125 | 1401 | 11 | 877 | 4.017 | 11.208 | Standard | Standard | Measured & Verified - Matheson Air Balancing
B Building | B311 | Flat Floor Classroom | 92 | 1544 | 11 | 1228 | 5.1038 | 16.7826 | Standard | Standard | Measured & Verified - Matheson Air Balancing
B Building | B316 | Computer Lab | 55 | 1703 | 11 | 0 | 0 | 30.9636 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
C/C1 Buildings | C1-053 | Special Purpose Teaching | 15 | 370 | 12 | 900 | 14.3084 | 24.6667 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C1-056 | Special Purpose Teaching | 15 | 340 | 12 | 900 | 15.5709 | 22.6667 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C1-057 | Special Purpose Teaching | 15 | 390 | 12 | 640 | 9.6531 | 26 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C1-058 | Special Purpose Teaching | 15 | 436 | 12 | 330 | 4.4522 | 29.0667 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C-102 | Special Purpose Teaching | 15 | 756 | 12 | 1620 | 12.605 | 50.4 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C-103 | Special Purpose Teaching | 15 | 567 | 12 | 1300 | 13.4869 | 37.8 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C-107 | Special Purpose Teaching | 15 | 688 | 12 | 1150 | 9.8324 | 45.8667 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C-234 | Special Purpose Teaching | 128 | 3340 | 12 | 5131 | 9.0366 | 26.0938 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C-248 | Computer Lab | 90 | 2462 | 12 | 2900 | 6.9288 | 27.3556 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C1-255 | Special Purpose Teaching | 40 | 1248 | 10.5 | 860 | 4.6326 | 31.2 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C-300 | Computer Lab | 25 | 850 | 9 | 500 | 4.6136 | 34 | Standard | Standard | Verified - HVAC design drawings
C/C1 Buildings | C1-365 | Tiered /Fixed Classroom | 15 | 380 | 11 | 560 | 9.4568 | 25.3333 | Standard | Standard | Verified - HVAC design drawings
Emera IDEA | 2005 | Special Purpose Teaching | 30 | 1229 | 11.5 | 1200 | 5.9933 | 40.9667 | Standard | Standard | Verified - HVAC design drawings
Emera IDEA | 3012 | Special Purpose Teaching | 64 | 2823 | 11.5 | 7080 | 15.3942 | 44.1094 | Standard | Standard | Verified - HVAC design drawings
D Building | D002 | Special Purpose Teaching | 30 | 1631 | 11 | 1480 | 5.823 | 54.3667 | Standard | Standard | Verified - HVAC design drawings
D Building | D004A | Special Purpose Teaching | 6 | 498 | 11 | 630 | 8.118 | 83 | Standard | Standard | Verified - HVAC design drawings
D Building | D010 | Special Purpose Teaching | 20 | 1655 | 11 | 1500 | 5.8161 | 82.75 | Standard | Standard | Verified - HVAC design drawings
D Building | D014 | Special Purpose Teaching | 25 | 1570 | 11 | 1680 | 6.8667 | 62.8 | Standard | Standard | Verified - HVAC design drawings
D Building | D102 | Special Purpose Teaching | 20 | 706 | 11 | 960 | 8.7258 | 35.3 | Standard | Standard | Verified - HVAC design drawings
D Building | D105 | Special Purpose Teaching | 50 | 1345 | 11 | 1380 | 6.5841 | 26.9 | Standard | Standard | Verified - HVAC design drawings
D Building | D115 | Special Purpose Teaching | 10 | 1159 | 11 | 1200 | 6.6441 | 115.9 | Standard | Standard | Verified - HVAC design drawings
D Building | D117 | Special Purpose Teaching | 10 | 1278 | 11 | 1800 | 9.0382 | 127.8 | Standard | Standard | Verified - HVAC design drawings
D Building | D203A | Flat Floor Classroom | 25 | 710 | 11 | 820 | 7.4113 | 28.4 | Standard | Standard | Verified - HVAC design drawings
D Building | D305A | Special Purpose Teaching | 12 | 705 | 11 | 1360 | 12.3791 | 58.75 | Standard | Standard | Verified - HVAC design drawings
D Building | D327 | Special Purpose Teaching | 20 | 1292 | 11 | 2730 | 13.5594 | 64.6 | Standard | Standard | Verified - HVAC design drawings
D Building | D406 | Flat Floor Classroom | 139 | 3000 | 11 | 3500 | 7.4866 | 21.5827 | Standard | Standard | Verified - HVAC design drawings
D Building | D410 | Flat Floor Classroom | 66 | 1427 | 11 | 2040 | 9.1737 | 21.6212 | Standard | Standard | Verified - HVAC design drawings
D Building | D501 | Tiered /Fixed Classroom | 62 | 932 | 11 | 1920 | 13.2198 | 15.0323 | Standard | Standard | Verified - HVAC design drawings
D Building | D503 | Special Purpose Teaching | 20 | 488 | 11 | 2000 | 26.2996 | 24.4 | Standard | Standard | Verified - HVAC design drawings
F Building | B010 | Special Purpose Teaching | 22 | 727 | 8.5 | 1400 | 15.9922 | 33.0455 | Standard | Standard | Verified - HVAC design drawings (100% OA)
F Building | B013 | Special Purpose Teaching | 15 | 822 | 8.5 | 2500 | 25.257 | 54.8 | Standard | Standard | Verified - HVAC design drawings (100% OA)
F Building | 1106 | Special Purpose Teaching | 10 | 864 | 9 | 1500 | 13.6166 | 86.4 | Standard | Standard | Verified - HVAC design drawings (100% OA)
F Building | 1113 | Classroom | 8 | 130 | 9 | 175 | 10.5581 | 16.25 | Standard | Standard | Verified - HVAC design drawings (100% OA)
F Building | 1114 | Special Purpose Teaching | 60 | 1937 | 9 | 4655 | 18.8486 | 32.2833 | Standard | Standard | Verified - HVAC design drawings (100% OA)
F Building | 2205 | Classroom | 6 | 118 | 9 | 200 | 13.2935 | 19.6667 | Standard | Standard | Verified - HVAC design drawings (100% OA)
F Building | 2206 | Classroom | 4 | 93 | 9 | 150 | 12.6502 | 23.25 | Standard | Standard | Verified - HVAC design drawings (100% OA)
F Building | 3303 | Special Purpose Teaching | 22 | 486 | 9 | 1095 | 17.6713 | 22.0909 | Standard | Standard | Verified - HVAC design drawings (100% OA)
G Building | G001 | Special Purpose Teaching | 60 | 2117 | 15 | 0 | 0 | 35.2833 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
G Building | G002D | Special Purpose Teaching | 10 | 126 | 8.5 | 295 | 19.4431 | 12.6 | Standard | Standard | Measured & Verified - Matheson Air Balancing
G Building | G004 | Special Purpose Teaching | 20 | 604 | 8.5 | 0 | 0 | 30.2 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
G Building | G006 | Special Purpose Teaching | 15 | 667 | 8.5 | 0 | 0 | 44.4667 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
G Building | G007 | Special Purpose Teaching | 20 | 548 | 8.5 | 201 | 3.046 | 27.4 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
G Building | G104 | Special Purpose Teaching | 8 | 428 | 14 | 0 | 0 | 53.5 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
G Building | G107 | Special Purpose Teaching | 6 | 574 | 14 | 0 | 0 | 95.6667 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
G Building | G210 | Computer Lab | 12 | 494 | 9 | 0 | 0 | 41.1667 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
G Building | G214 | Flat Floor Classroom | 42 | 788 | 12 | 0 | 0 | 18.7619 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
G Building | G215 | Classroom | 25 | 543 | 12 | 0 | 0 | 21.72 | Standard | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
Medjuck (H) | HA18 | Tiered /Fixed Classroom | 46 | 708 | 9 | 204 | 2.2599 | 15.3913 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
Medjuck (H) | HA19 | Tiered /Fixed Classroom | 120 | 1837 | 10 | 5454 | 20.9574 | 15.3083 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
Medjuck (H) | HA33 | Special Purpose Teaching | 4 | 258 | 9 | 365 | 11.0959 | 64.5 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
Medjuck (H) | HB1 | Classroom | 12 | 231 | 9 | 108 | 3.6669 | 19.25 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
Medjuck (H) | HB2 | Flat Floor Classroom | 35 | 593 | 9 | 342 | 4.5234 | 16.9429 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
Medjuck (H) | HB3A | Special Purpose Teaching | 14 | 428 | 8 | 72 | 1.4843 | 30.5714 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
Medjuck (H) | HB4 | Tiered /Fixed Classroom | 55 | 693 | 9.5 | 386 | 4.1387 | 12.6 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
Medjuck (H) | HB21 | Special Purpose Teaching | 100 | 2527 | 12 | 1900 | 4.4228 | 25.27 | Measurement & Verification Required | Standard | Measured & Verified - In-house HVAC technicians
Medjuck (H) | HD1 & HD1A | Special Purpose Teaching | 52 | 3624 | 20 | 705 | 0.6866 | 69.6923 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
Medjuck (H) | HD2A | Special Purpose Teaching | 20 | 1514 | 12.5 | 1033 | 3.853 | 75.7 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
Medjuck (H) | HD2D | Special Purpose Teaching | 20 | 400 | 9 | 95 | 1.8627 | 20 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
Medjuck (H) | HD3 & HD3A | Special Purpose Teaching | 52 | 3149 | 20 | 887 | 0.99415 | 60.5577 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
Medjuck (H) | HD4 | Classroom | 12 | 307 | 9.5 | 75 | 1.8152 | 25.5833 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
Medjuck (H) | HE1A | Special Purpose Teaching | 21 | 1530 | 10 | 815 | 3.7601 | 72.8571 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
O'Brien Hall | 700 | Special Purpose Teaching | 24 | 967 | 8 | 132 | 1.2045 | 40.2917 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
O'Brien Hall | 705 | Special Purpose Teaching | 16 | 512 | 8 | 266 | 4.5841 | 32 | Measurement & Verification Required | Standard | Measured & Verified - Matheson Air Balancing
O'Brien Hall | 715 | Special Purpose Teaching | 24 | 718 | 8 | 257 | 3.1583 | 29.9167 | Measurement & Verification Required | Sub Standard | Measured & Verified - Matheson Air Balancing (requires HVAC Improvements)
N Building | N125 | Special Purpose Teaching | 4 | 500 | 10 | 184 | 2.5976 | 125 | Standard | Sub Standard | Measured & Verified - In-house HVAC Technicians (100% OA) (requires HVAC improvements)
N Building | N126 | Special Purpose Teaching | 23 | 1795 | 17.25 | 1734 | 3.953 | 78.0435 | Standard | Standard | Measured & Verified - In-house HVAC Technicians (100% OA)
N Building | N201 | Special Purpose Teaching | 20 | 4232 | 9 | 2940 | 5.4487 | 211.6 | Standard | Standard | Measured & Verified - In-house HVAC Technicians (100% OA)
N Building | N310 | Special Purpose Teaching | 5 | 671 | 9 | 727 | 8.4977 | 134.2 | Standard | Standard | Measured & Verified - In-house HVAC Technicians (100% OA)
N Building | N321 | Special Purpose Teaching | 35 | 1387 | 8.25 | 1014 | 6.2552 | 39.6286 | Standard | Standard | Measured & Verified - In-house HVAC Technicians (100% OA)
Ind Engineering Add | 020 | Special Purpose Teaching | 50 | 1640 | 9 | 2200 | 10.5213 | 32.8 | Standard | Standard | Verified - HVAC design drawings
Ind Engineering Add | 021 | Special Purpose Teaching | 68 | 1585 | 9 | 1590 | 7.8679 | 23.3088 | Standard | Standard | Verified - HVAC design drawings
Ind Engineering Add | 120 | Flat Floor Classroom | 56 | 1157 | 9 | 1900 | 12.8798 | 20.6607 | Standard | Standard | Verified - HVAC design drawings
Ind Engineering Add | 121 | Flat Floor Classroom | 90 | 1600 | 9 | 4200 | 20.5882 | 17.7778 | Standard | Standard | Verified - HVAC design drawings
Ind Engineering Add | 220 | Tiered /Fixed Classroom | 50 | 1602 | 9 | 3180 | 15.5688 | 32.04 | Standard | Standard | Verified - HVAC design drawings
Ind Engineering Add | 221 | Computer Lab | 37 | 868 | 9 | 2000 | 18.0717 | 23.4595 | Standard | Standard | Verified - HVAC design drawings
Ind Engineering Add | 222 | Tiered /Fixed Classroom | 52 | 802 | 9 | 1650 | 16.1361 | 15.4231 | Standard | Standard | Verified - HVAC design drawings
Morroy | 310 | Classroom | 24 | 743 | 11 | 500 | 4.3184 | 30.9583 | Standard | Standard | Verified - HVAC design drawings
Design | G109 | Tiered /Fixed Classroom | 450 | 2206 | 16 | 10500 | 20.9989 | 4.9022 | Standard | Standard | Verified - HVAC design drawings
Design | 3105 | Special Purpose Teaching | 88 | 5431 | 16 | 1510 | 1.2266 | 61.7159 | Standard | Sub Standard | Verified - HVAC design drawings (100% OA) - investigating with Design Engineer
Design | 3105A | Classroom | 8 | 212 | 15.5 | 180 | 3.8667 | 26.5 | Standard | Standard | Verified - HVAC design drawings (100% OA)
Design | 3105C | Classroom | 8 | 212 | 10 | 199 | 6.626 | 26.5 | Standard | Standard | Verified - HVAC design drawings (100% OA)
Assumptions & Notes:
1) List of learning spaces provided by FM Space management team
2) Pre-COVID room capacities were collected from Campus Space Database
3) Room area data collected from Campus Space Database
4) Room height data collected physically using a laser measure
5) All Air Flow (CFM) measurements are total air flow supplied to the room (fresh air + recirculated filtered air)
6) Standard air flow is considered as total flow of 3 ACH or greater.
7) To calculate the functional volume of a classroom, 15% was deducted from each room for dead space (furniture, equipment, built-ins, people,etc)
8) Original HVAC assessment included assessing the capabilities of the ventilation systems at the building level.

## Dal AC
Classroom HVAC Master Sheet - Agriculture Campus (updated August 12th)
Building Name | Room Number | Room Type | Pre-COVID Capacity | Plan Area (sq.ft) | Room Height (ft) | Air Flow (CFM) | Air Changes per Hr (ACH) | Ocuppant Density | 0riginal HVAC Assessment | Post Verification Assessment | Source of Air Volume Data
AGRICULTURAL COX INSTITUTE | 106 | Special Purpose Teaching | 14 | 1210 | 10 | 1200 | 7.0005 | 86.4286 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 112 | Special Purpose Teaching | 24 | 1258 | 9.6 | 1200 | 7.0139 | 52.4167 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 115 | Special Purpose Teaching | 24 | 202 | 9.2 | 200 | 7.5967 | 8.4167 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 121 | Computer Lab | 20 | 723 | 9 | 750 | 8.136 | 36.15 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 130 | Special Purpose Teaching | 18 | 232 | 10 | 200 | 6.0852 | 12.8889 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 134 | Tiered /Fixed Classroom | 165 | 1850 | 12.4 | 3000 | 9.2312 | 11.2121 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 153 | Flat Floor Classroom | 108 | 1506 | 12.5 | 5100 | 19.1235 | 13.9444 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 154 | Classroom | 4 | 103 | 8.5 | 150 | 12.0939 | 25.75 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 157 | Flat Floor Classroom | 56 | 1258 | 13 | 2500 | 10.7907 | 22.4643 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 158 | Classroom | 4 | 101 | 8.6 | 150 | 12.19 | 25.25 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 160 | Classroom | 4 | 106 | 8.5 | 150 | 11.7516 | 26.5 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 162 | Classroom | 4 | 105 | 8.5 | 150 | 11.8636 | 26.25 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 170 | Special Purpose Teaching | 36 | 1017 | 8.5 | 2181 | 17.8094 | 28.25 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 175 | Classroom | 8 | 231 | 8.3 | 300 | 11.0449 | 28.875 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 177 | Classroom | 11 | 245 | 8.5 | 300 | 10.1688 | 22.2727 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 179 | Classroom | 20 | 733 | 8.3 | 700 | 8.1217 | 36.65 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 180 | Computer Lab | 45 | 1741 | 13 | 4200 | 13.099 | 38.6889 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 184 | Flat Floor Classroom | 32 | 861 | 13 | 2300 | 14.5049 | 26.9062 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 200 | Classroom | 17 | 1711 | 9 | 2400 | 11.0015 | 100.6471 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 206 | Special Purpose Teaching | 36 | 780 | 9 | 900 | 9.0498 | 21.6667 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 208 | Flat Floor Classroom | 31 | 343 | 9 | 300 | 6.8599 | 11.0645 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 216 | Special Purpose Teaching | 40 | 1246 | 10 | 1200 | 6.7982 | 31.15 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 222 | Special Purpose Teaching | 16 | 96 | 8 | 100 | 9.1912 | 6 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 228 | Special Purpose Teaching | 24 | 310 | 9.6 | 400 | 9.4877 | 12.9167 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 240 | Special Purpose Teaching | 1 | 974 | 10 | 1200 | 8.6967 | 974 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 251 | Special Purpose Teaching | 30 | 1066 | 8.5 | 1772 | 13.8045 | 35.5333 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 254 | Flat Floor Classroom | 16 | 868 | 8.5 | 999 | 9.5578 | 54.25 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 255 | Special Purpose Teaching | 30 | 1175 | 8.5 | 1936 | 13.683 | 39.1667 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 257 | Special Purpose Teaching | 24 | 935 | 8.5 | 1528 | 13.5714 | 38.9583 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 275 | Special Purpose Teaching | 16 | 781 | 8.5 | 1943 | 20.6602 | 48.8125 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 277 | Special Purpose Teaching | 36 | 1132 | 8 | 1626 | 12.6741 | 31.4444 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 281 | Special Purpose Teaching | 6 | 301 | 8.6 | 444 | 12.1074 | 50.1667 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 300 | Classroom | 17 | 372 | 10 | 400 | 7.5901 | 21.8824 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 330 | Special Purpose Teaching | 16 | 1139 | 9 | 3400 | 23.4124 | 71.1875 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 342 | Special Purpose Teaching | 16 | 972 | 9 | 1500 | 12.1036 | 60.75 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 350 | Special Purpose Teaching | 6 | 580 | 8.5 | 1597 | 22.866 | 96.6667 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 352 | Special Purpose Teaching | 6 | 616 | 8.5 | 1340 | 18.065 | 102.6667 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 354 | Classroom | 16 | 885 | 13 | 1850 | 11.3506 | 55.3125 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 356 | Classroom | 21 | 608 | 13 | 1750 | 15.6287 | 28.9524 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 358 | Classroom | 24 | 516 | 13 | 1475 | 15.5214 | 21.5 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 360 | Classroom | 24 | 486 | 13 | 1475 | 16.4795 | 20.25 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 370 | Special Purpose Teaching | 24 | 1543 | 8.5 | 3150 | 16.9534 | 64.2917 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 374 | Special Purpose Teaching | 24 | 1455 | 8.5 | 2920 | 16.6661 | 60.625 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 377 | Special Purpose Teaching | 24 | 1554 | 8.5 | 2296 | 12.2697 | 64.75 | Standard | Standard | Verified - HVAC design drawings
AGRICULTURAL COX INSTITUTE | 383 | Flat Floor Classroom | 146 | 2020 | 13 | 4800 | 12.9026 | 13.8356 | Standard | Standard | Verified - HVAC design drawings
BANTING BUILDING | 2 | Special Purpose Teaching | 15 | 2726 | 18 | 0 | 0 | 181.7333 | Standard | Sub Standard | Measured and Verified - Matheson Air Balancing (requires HVAC improvements)
BANTING BUILDING | 5 | Special Purpose Teaching | 4 | 855 | 18 | 0 | 0 | 213.75 | Standard | Sub Standard | Measured and Verified - Matheson Air Balancing (requires HVAC improvements)
BANTING BUILDING | 6A | Special Purpose Teaching | 15 | 1037 | 18 | 0 | 0 | 69.1333 | Standard | Sub Standard | Measured and Verified - Matheson Air Balancing (requires HVAC improvements)
BANTING BUILDING | 7 | Classroom | 15 | 439 | 10 | 0 | 0 | 29.2667 | Standard | Sub Standard | Measured and Verified - Matheson Air Balancing (requires HVAC improvements)
BANTING BUILDING | 9 | Special Purpose Teaching | 15 | 3421 | 18 | 0 | 0 | 228.0667 | Standard | Sub Standard | Measured and Verified - Matheson Air Balancing (requires HVAC improvements)
BANTING BUILDING | 25 | Flat Floor Classroom | 52 | 995 | 10 | 1784 | 12.6562 | 19.1346 | Standard | Standard | Measured and Verified - Matheson Air Balancing
BANTING BUILDING | 32 | Flat Floor Classroom | 34 | 667 | 10 | 1136 | 12.0222 | 19.6176 | Standard | Standard | Measured and Verified - Matheson Air Balancing
BANTING BUILDING | 33 | Computer Lab | 24 | 1158 | 10 | 1217 | 7.4185 | 48.25 | Standard | Standard | Measured and Verified - Matheson Air Balancing
BANTING BUILDING | 50 | Computer Lab | 4 | 275 | 10 | 370 | 9.4973 | 68.75 | Standard | Standard | Measured and Verified - Matheson Air Balancing
BOULDEN BUILDING | 12 | Special Purpose Teaching | 12 | 606 | 8.5 | 634 | 8.6882 | 50.5 | Standard | Standard | Measured and Verified - Matheson Air Balancing
BOULDEN BUILDING | 15 | Special Purpose Teaching | 12 | 285 | 8.5 | 290 | 8.4502 | 23.75 | Standard | Standard | Measured and Verified - Matheson Air Balancing
BOULDEN BUILDING | 16 | Special Purpose Teaching | 12 | 269 | 10 | 321 | 8.4234 | 22.4167 | Standard | Standard | Measured and Verified - Matheson Air Balancing
COLLINS BUILDING | 105 | Computer Lab | 24 | 942 | 11 | 0 | 0 | 39.25 | Measurement & Verification Required | Sub Standard | Measured and Verified - In-house technicians (requires HVAC improvements)
COLLINS BUILDING | 110 | Flat Floor Classroom | 30 | 706 | 12 | 0 | 0 | 23.5333 | Measurement & Verification Required | Sub Standard | Measured and Verified - In-house technicians (requires HVAC improvements)
CUMMING HALL | 125 | Tiered /Fixed Classroom | 415 | 2878 | 16 | 8121 | 12.4489 | 6.9349 | Standard | Standard | Measured and Verified - Matheson Air Balancing
CUMMING HALL | 203 | Classroom | 12 | 1268 | 17 | 1200 | 3.9296 | 105.6667 | Standard | Standard | Measured and Verified - Matheson Air Balancing
ENG EXT-CENTRAL HEATING PLANT | 205 | Special Purpose Teaching | 8 | 530 | 9 | 645 | 9.545 | 66.25 | Standard | Standard | Verified - HVAC design drawings (100% OA)
ENG EXT-CENTRAL HEATING PLANT | 208 | Special Purpose Teaching | 15 | 975 | 9 | 760 | 6.1136 | 65 | Standard | Standard | Verified - HVAC design drawings (100% OA)
ENG EXT-CENTRAL HEATING PLANT | 212 | Special Purpose Teaching | 45 | 3211 | 9 | 2890 | 7.0591 | 71.3556 | Standard | Standard | Verified - HVAC design drawings (100% OA)
ENG EXT-CENTRAL HEATING PLANT | 219 | Classroom | 10 | 337 | 9 | 310 | 7.2148 | 33.7 | Standard | Standard | Verified - HVAC design drawings (100% OA)
ENG EXT-CENTRAL HEATING PLANT | 226 | Classroom | 12 | 298 | 9 | 185 | 4.8691 | 24.8333 | Standard | Standard | Verified - HVAC design drawings (100% OA)
HALEY INSTITUTE | 106 | Special Purpose Teaching | 24 | 1107 | 8.5 | 1750 | 13.1282 | 46.125 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 110 | Tiered /Fixed Classroom | 43 | 731 | 9 | 1200 | 12.8752 | 17 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 111 | Special Purpose Teaching | 31 | 713 | 10 | 1000 | 9.9002 | 23 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 112 | Special Purpose Teaching | 32 | 722 | 9 | 1100 | 11.9494 | 22.5625 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 114 | Flat Floor Classroom | 48 | 870 | 9 | 1625 | 14.6495 | 18.125 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 116 | Flat Floor Classroom | 60 | 994 | 9 | 1500 | 11.8357 | 16.5667 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 161 | Special Purpose Teaching | 20 | 1045 | 9 | 1148 | 8.6162 | 52.25 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 200 | Tiered /Fixed Classroom | 120 | 2493 | 17 | 4500 | 7.495 | 20.775 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 215 | Special Purpose Teaching | 6 | 282 | 9 | 400 | 11.125 | 47 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 225 | Special Purpose Teaching | 24 | 1472 | 8.5 | 2100 | 11.8474 | 61.3333 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 228 | Computer Lab | 20 | 922 | 9 | 1400 | 11.9093 | 46.1 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 230 | Special Purpose Teaching | 20 | 1487 | 9 | 2100 | 11.0764 | 74.35 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 233 | Special Purpose Teaching | 12 | 1265 | 9 | 1800 | 11.1602 | 105.4167 | Standard | Standard | Verified - HVAC design drawings
HALEY INSTITUTE | 254 | Flat Floor Classroom | 43 | 1033 | 9 | 1000 | 7.5926 | 24.0233 | Standard | Standard | Verified - HVAC design drawings
LANGILLE ATHLETIC CENTRE | 205 | Flat Floor Classroom | 30 | 623 | 9.5 | 430 | 5.1285 | 20.7667 | Standard | Standard | Measured and Verified - Matheson Air Balancing
MACRAE LIBRARY | 13 | Classroom | 12 | 315 | 9 | 257 | 6.399 | 26.25 | Standard | Standard | Measured and Verified - Matheson Air Balancing
MACRAE LIBRARY | 14 | Classroom | 10 | 224 | 9 | 238 | 8.3333 | 22.4 | Standard | Standard | Measured and Verified - Matheson Air Balancing
MACRAE LIBRARY | 15 | Classroom | 10 | 224 | 9 | 248 | 8.6835 | 22.4 | Standard | Standard | Measured and Verified - Matheson Air Balancing
MACRAE LIBRARY | 106 | Flat Floor Classroom | 90 | 1425 | 9 | 1399 | 7.7 | 15.8333 | Standard | Standard | Measured and Verified - Matheson Air Balancing
MACRAE LIBRARY | 218 | Classroom | 24 | 1066 | 9 | 1468 | 10.8009 | 44.4167 | Standard | Standard | Measured and Verified - Matheson Air Balancing
MACRAE LIBRARY | 219 | Classroom | 24 | 1066 | 9 | 2035 | 14.9726 | 44.4167 | Standard | Standard | Measured and Verified - Matheson Air Balancing
RUMINANT ANIMAL CENTRE | 102 | Special Purpose Teaching | 24 | 1104 | 10 | 1896 | 12.1228 | 46 | Standard | Standard | Measured and Verified - Matheson Air Balancing
RUMINANT ANIMAL CENTRE | 260 | Classroom | 24 | 900 | 10 | 1846 | 14.4784 | 37.5 | Standard | Standard | Measured and Verified - Matheson Air Balancing
RURAL RESEARCH CENTRE | 4 | Cassroom | 35 | 625 | 8 | 500 | 7.0588 | 17.8571 | Standard | Standard | Verified - HVAC design drawings (100% OA)
Assumptions & Notes:
1) List of learning spaces provided by FM Space management team
2) Pre-COVID room capacities were collected from Campus Space Database
3) Room area data collected from Campus Space Database
4) Room height data collected physically using a laser measure
5) All Air Flow (CFM) measurements are total air flow supplied to the room (fresh air + recirculated filtered air)
6) Standard air flow is considered as total flow of 3 ACH or greater.
7) To calculate the functional volume of a classroom, 15% was deducted from each room for dead space (furniture, equipment, built-ins, people,etc)
8) Original HVAC assessment included assessing the capabilities of the ventilation systems at the building level.